## all_data
From NEEP: http://www.neep.org/initiatives/high-efficiency-products/emerging-technologies/ashp/cold-climate-air-source-heat-pump | [46 empty] | From NEEP:
Manufacturer | Brand (if applicable) | Model Name | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | AHRI Type | HSPF (Region IV): | SEER | EER (@ 95°F) | Cooling Capacity (Btuh) | ENERGY STAR Certified | Ductless or Centrally Ducted | If Ductless, Multi-zone or Single-zone? | Ductless Indoor Type |  | Minimum Capacity 47°F | Rated Capacity 47°F | Maximum Capacity 47°F | Input Power at Min. Capcaity 47°F | Rated Input Power 47°F | Input Power at Max. Capacity 47°F | COP at Min. Capacity 47°F | COP at Rated Capacity 47°F | COP at Max. Capacity 47°F |  | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | Input Power at Min. Capacity 17°F | Input Power at Rated Capacity 17°F | Input Power at Max. Capacity 17°F | COP at Min. Capacity 17°F | COP at Rated Capacity 17°F | COP at Max. Capacity 17°F |  | Minimum Capacity 5°F |  | Maximum Capacity 5°F | Input Power at Min. Capacity 5°F |  | Input Power at Max. Capacity 5°F | COP at Min. Capacity 5°F |  | COP at Max. Capacity 5°F |  | Maintenance Capacity (Max 5°F/Max 47°F) | Maintenance Capacity (Max 5°F/Max 17°F) |  | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? |  | Outdoor Dry Bulb (°F) | Minimum Capactity X°F |  | Maximum Capacity X°F | Input Power at Min. Capacity X°F |  | Input Power at Max. Capacity X°F | COP at Min. Capacity X°F |  | COP at Max. Capacity X°F
C1 | C2 | C3 | ahri | out_model | in_model | C7 | hspf | C9 | C10 | C11 | C12 | C13 | C14 | C15 | C16 | cap_min_47 | cap_rated_47 | cap_max_47 | C20 | C21 | C22 | cop_min_47 | cop_rated_47 | cop_max_47 | C26 | cap_min_17 | cap_rated_17 | cap_max_17 | C30 | C31 | C32 | cop_min_17 | cop_rated_17 | cop_max_17 | C36 | cap_min_5 | C38 | cap_max_5 | C40 | C41 | C42 | cop_min_5 | C44 | cop_max_5 | C46 | C47 | C48 | C49 | C50 | C51 | C52 | C53 | dbt_cold | cap_min_cold | C56 | cap_max_cold | C58 | C59 | C60 | cop_min_cold | C62 | cop_max_cold
Daikin AC (Americas), Inc | Daikin | MXS Series | 8103542 | 2MXS18NMVJU | CTXS09HVJU+CTXS09LVJU | HMSV-A-CB | 10.7 | 18.9 | 12.5 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 4900 | 18900 | 25000 | 0.29 | 1.26 | 1.69 | 4.94 | 4.4 | 4.34 |  | 3800 | 12780 | 16910 | 0.29 | 1.11 | 1.49 | 3.8404 | 3.37 | 3.33 |  | 3190 |  | 13150 | 0.29 |  | 1.4 | 3.21 |  | 2.76 |  | 0.526 | 0.77765 |  | Accessory (KEH063A4E) |  | Temp. below 23 degrees |  | 0 | 2910 | z | 11580 | 0.29 |  | 1.36 | 2.93 |  | 2.5
Daikin AC (Americas), Inc | Daikin | MXS Series | 8103869 | 3MXS24NMVJU | CTXS07LVJU+CTXS09LVJU+CTXS09LVJU | HMSV-A-CB | 12.5 | 17.9 | 12.7 | 24000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 8500 | 24000 | 36000 | 0.43 | 1.46 | 2.97 | 5.79 | 4.82 | 3.55 |  | 6570 | 16230 | 24350 | 0.43 | 1.29 | 2.62 | 4.478 | 3.69 | 2.72 |  | 5500 |  | 18930 | 0.43 |  | 2.46 | 3.75 |  | 2.26 |  | 0.52583 | 0.77741 |  | Accessory (KEH063A4E) |  | Temp. below 23 degrees |  | 0 | 5020 | z | 16670 | 0.43 |  | 2.39 | 3.42 |  | 2.05
Daikin AC (Americas), Inc | Daikin | MXL Aurora Series | 8849535 | 2MXL18QMVJU | 40GRQB18H--301 | HMSV-A-CB | 10.3 | 17 | 12.7 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 7710 | 18940 | 36000 | 0.47 | 1.32 | 3.17 | 4.81 | 4.21 | 3.33 |  | 5020 | 12330 | 23480 | 0.41 | 1.15 | 2.77 | 3.5885 | 3.14 | 2.48 |  | 4050 |  | 18930 | 0.39 |  | 2.62 | 3.04 |  | 2.12 |  | 0.52583 | 0.80622 |  | N/A |  |  |  | N/A
Daikin AC (Americas), Inc | Daikin | MXL Aurora Series | 8849539 | 3MXL24QMVJU | CTXS07LVJU+FTXS09LVJU+FTXS09LVJU | HMSV-A-CB | 12.5 | 17.9 | 12.7 | 24000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 7720 | 24000 | 41000 | 0.44 | 1.54 | 3.52 | 5.14 | 4.57 | 3.41 |  | 5030 | 15670 | 26780 | 0.38 | 1.35 | 3.08 | 3.8795 | 3.4 | 2.55 |  | 4060 |  | 21600 | 0.36 |  | 2.92 | 3.31 |  | 2.17 |  | 0.52683 | 0.80657 |  | N/A |  |  |  | N/A
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324709 | DZ20VC0241B | CA*F3642*6D*+MBVC1200**-1A*+TXV | HRCU-A-CB | 10 | 21 | 13 | 23400 | Yes | Centrally Ducted | N/A | N/A |  | 5188 | 23400 | 23959 | 0.324 | 2.063 | 1.995 | 4.6928 | 3.3242 | 3.5196 |  | 1420 | 13000 | 14990 | 0.336 | 1.465 | 1.71 | 1.2386 | 2.6006 | 2.5691 |  | 958 |  | 11648 | 0.377 |  | 1.597 | 0.74473 |  | 2.1376 |  | 0.48616 | 0.77705 |  | N/A |  |  |  | N/A
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324709 | DZ20VC0241B | CA*F3642*6D*+MBVC1200**-1A*+TXV | HRCU-A-CB | 10 | 21 | 13 | 23400 | Yes | Centrally Ducted | N/A | N/A |  | 5507 | 23600 | 23600 | 0.33 | 1.87 | 1.87 | 4.91 | 3.7 | 3.7 |  | 3943 | 13915 | 15200 | 0.338 | 1.487 | 1.82 | 3.419 | 2.74 | 2.45 |  | 1650 |  | 11400 | 0.296 |  | 1.6 | 1.63 |  | 2.09 |  | 0.48305 | 0.75 |  | N/A |  |  |  | N/A
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324711 | DZ20VC0361B | CA*F3743*6D*+MBVC1600**-1A*+TXV | HRCU-A-CB | 10 | 21 | 14 | 35400 | Yes | Centrally Ducted | N/A | N/A |  | 13438 | 35000 | 35000 | 0.721 | 2.48 | 2.48 | 5.46 | 4.14 | 4.14 |  | 8580 | 18365 | 28800 | 0.722 | 2.092 | 3.72 | 3.4829 | 2.57 | 2.27 |  | 5135 |  | 22100 | 0.722 |  | 3.48 | 2.08 |  | 1.86 |  | 0.63143 | 0.76736 |  | N/A |  |  |  | N/A
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324713 | DZ20VC0481B | CA*F4961*6D*+MBVC2000**-1A*+TXV | HRCU-A-CB | 10 | 20 | 13 | 46500 | Yes | Centrally Ducted | N/A | N/A |  | 13274 | 45500 | 45500 | 0.796 | 3.42 | 3.42 | 4.88 | 3.9 | 3.9 |  | 8394 | 28254 | 34000 | 0.766 | 2.926 | 4.15 | 3.2117 | 2.83 | 2.4 |  | 5390 |  | 26000 | 0.722 |  | 3.87 | 2.19 |  | 1.97 |  | 0.57143 | 0.76471 |  | N/A |  |  |  | N/A
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324715 | DZ20VC0601B | CA*F4961*6D*+MBVC2000**-1A*+TXV | HRCU-A-CB | 10 | 20 | 12.5 | 52500 | Yes | Centrally Ducted | N/A | N/A |  | 15848 | 50000 | 50000 | 0.891 | 3.76 | 3.76 | 5.21 | 3.9 | 3.9 |  | 9302 | 32293 | 34000 | 0.92 | 3.466 | 4.07 | 2.96 | 2.73 | 2.45 |  | 5407 |  | 26000 | 0.901 |  | 3.85 | 1.76 |  | 1.98 |  | 0.52 | 0.76471 |  | N/A |  |  |  | N/A
Daikin AC (Americas), Inc | Daikin | Quaternity Series | 3208521 | RXG09HVJU | FTXG09HVJU | HRCU-A-CB-O | 11 | 26.1 | 15.8 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4668 | 12000 | 18670 | 0.224 | 0.78 | 1.94 | 6.11 | 4.51 | 2.82 |  | 3003 | 8100 | 12170 | 0.194 | 0.72 | 1.68 | 4.54 | 3.3 | 2.12 |  | 2330 |  | 9460 | 0.182 |  | 1.57 | 3.75 |  | 1.77 |  | 0.5067 | 0.77732 |  | Accessory (KEH041A45) |  | Temp. below 23 degrees |  | -4 |  | z | 7430 |  |  | 1.49 |  |  | 1.46
Daikin AC (Americas), Inc | Daikin | Quaternity Series | 3208522 | RXG12HVJU | FTXG12HVJU | HRCU-A-CB-O | 10.55 | 24.2 | 14 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4668 | 16000 | 19130 | 0.224 | 1.16 | 2.14 | 6.11 | 4.04 | 2.62 |  | 3003 | 10400 | 12920 | 0.192 | 0.98 | 1.78 | 4.58 | 3.1 | 2.13 |  | 2330 |  | 10040 | 0.181 |  | 1.67 | 3.77 |  | 1.76 |  | 0.52483 | 0.77709 |  | Accessory (KEH041A45) |  | Temp. below 23 degrees |  | -4 |  | z | 7880 |  |  | 1.58 |  |  | 1.46
Daikin AC (Americas), Inc | Daikin | Quaternity Series | 3208523 | RXG15HVJU | FTXG15HVJU | HRCU-A-CB-O | 10 | 21 | 12.9 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4668 | 18000 | 21280 | 0.234 | 1.32 | 2.16 | 5.85 | 3.99 | 2.89 |  | 3003 | 11100 | 14340 | 0.203 | 1.08 | 1.87 | 4.34 | 3 | 2.25 |  | 2330 |  | 11150 | 0.19 |  | 1.75 | 3.59 |  | 1.87 |  | 0.52397 | 0.77755 |  | Accessory (KEH041A45) |  | Temp. below 23 degrees |  | -4 |  | z | 8750 |  |  | 1.67 |  |  | 1.54
Daikin AC (Americas), Inc | Daikin | LV Series | 5265753 | RXS09LVJU | FTXS09LVJU | HRCU-A-CB-O | 12.5 | 24.5 | 15.3 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4400 | 12000 | 15600 | 0.22 | 0.79 | 1.27 | 5.99 | 4.45 | 3.6 |  | 2408 | 6520 | 8465 | 0.15 | 0.55 | 0.88 | 4.72 | 3.48 | 2.81 |  | 1982 |  | 6968 | 0.14 |  | 0.84 | 4.08 |  | 2.43 |  | 0.44667 | 0.82315 |  | Accessory (KEH041A41) |  | Temp. below 23 degrees |  | 0 | 1727 | z | 6070 | 0.14 |  | 0.82 | 3.66 |  | 2.18
Daikin AC (Americas), Inc | Daikin | LV Series | 5265755 | RXS12LVJU | FTXS12LVJU | HRCU-A-CB-O | 12.5 | 23 | 12.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4800 | 14400 | 18000 | 0.22 | 0.97 | 1.27 | 6.53 | 4.35 | 4.15 |  | 2593 | 7816 | 9780 | 0.15 | 0.67 | 0.88 | 5.08 | 3.4 | 3.25 |  | 2135 |  | 8051 | 0.14 |  | 0.84 | 4.39 |  | 2.81 |  | 0.44728 | 0.82321 |  | Accessory (KEH041A41) |  | Temp. below 23 degrees |  | 0 | 1860 | z | 7013 | 0.14 |  | 0.82 | 3.94 |  | 2.52
Daikin AC (Americas), Inc | Daikin | LV Series | 5265756 | RXS15LVJU | FTXS15LVJU | HRCU-A-CB-O | 11.6 | 20.6 | 14.4 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 5800 | 18000 | 22300 | 0.39 | 1.32 | 1.64 | 4.35 | 4 | 3.97 |  | 3149 | 9780 | 12114 | 0.27 | 0.92 | 1.14 | 3.4 | 3.13 | 3.11 |  | 2592 |  | 9972 | 0.26 |  | 1.09 | 2.94 |  | 2.69 |  | 0.44717 | 0.82318 |  | Accessory (KEH041A42) |  | Temp. below 23 degrees |  | 0 | 2258 | z | 8687 | 0.25 |  | 1.06 | 2.64 |  | 2.41
Daikin AC (Americas), Inc | Daikin | LV Series | 5265757 | RXS18LVJU | FTXS18LVJU | HRCU-A-CB-O | 11 | 20.3 | 12.7 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 5800 | 21600 | 26700 | 0.41 | 1.71 | 2.12 | 4.17 | 3.7 | 3.7 |  | 3149 | 11725 | 14485 | 0.28 | 1.19 | 1.47 | 3.26 | 2.89 | 2.89 |  | 2592 |  | 11924 | 0.27 |  | 1.4 | 2.82 |  | 2.49 |  | 0.44659 | 0.8232 |  | Accessory (KEH041A42) |  | Temp. below 23 degrees |  | 0 | 2258 | z | 10387 | 0.26 |  | 1.36 | 2.53 |  | 2.24
Daikin AC (Americas), Inc | Daikin | LV Series | 5265758 | RXS24LVJU | FTXS24LVJU | HRCU-A-CB-O | 10.6 | 20 | 12.5 | 21400 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 7800 | 25400 | 31400 | 0.54 | 2.21 | 2.75 | 4.25 | 3.37 | 3.34 |  | 4260 | 13781 | 17041 | 0.37 | 1.54 | 1.91 | 3.34 | 2.63 | 2.61 |  | 3507 |  | 14028 | 0.36 |  | 1.82 | 2.89 |  | 2.26 |  | 0.44675 | 0.82319 |  | Accessory (KEH041A43) |  | Temp. below 23 degrees |  | 0 | 3055 | z | 12220 | 0.35 |  | 1.77 | 2.59 |  | 2.03
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849330 | RXL15QMVJU | FTX15NMVJU | HRCU-A-CB-O | 12.5 | 20 | 13 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 5814 | 18295 | 24566 | 0.39 | 1.341 | 2.307 | 4.37 | 4 | 3.12 |  | 3784 | 11904 | 19755 | 0.341 | 1.17 | 2.361 | 3.25 | 2.98 | 2.45 |  | 2958 |  | 18254 | 0.32 |  | 2.361 | 2.71 |  | 2.27 |  | 0.74306 | 0.92402 |  | N/A |  |  |  | N/A |  | z
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849445 | RXL15QMVJU | FVXS15NVJU | HRCU-A-CB-O | 11.3 | 20 | 12.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 5814 | 18056 | 23884 | 0.34 | 1.401 | 1.809 | 5.01 | 3.78 | 3.87 |  | 3784 | 11751 | 19414 | 0.297 | 1.222 | 2.105 | 3.73 | 2.82 | 2.7 |  | 2958 |  | 18015 | 0.279 |  | 2.198 | 3.11 |  | 2.4 |  | 0.75427 | 0.92794 |  | N/A |  |  |  | N/A |  | z
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849458 | RXL12QMVJU | FTX12NMVJU | HRCU-A-CB-O | 12 | 20 | 12.5 | 10900 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4446 | 13679 | 18766 | 0.24 | 1.026 | 1.562 | 5.43 | 3.91 | 3.52 |  | 2893 | 8902 | 15388 | 0.21 | 0.895 | 1.789 | 4.04 | 2.92 | 2.52 |  | 2262 |  | 14330 | 0.197 |  | 1.86 | 3.37 |  | 2.26 |  | 0.76362 | 0.93125 |  | N/A |  |  |  | N/A |  | z
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849459 | RXL09QMVJU | FVXS09NVJU | HRCU-A-CB-O | 11.7 | 20 | 12.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4446 | 10089 | 14330 | 0.24 | 0.721 | 1.356 | 5.43 | 4.1 | 3.1 |  | 2893 | 6565 | 11082 | 0.21 | 0.629 | 1.378 | 4.04 | 3.06 | 2.36 |  | 2262 |  | 10065 | 0.197 |  | 1.384 | 3.37 |  | 2.13 |  | 0.70237 | 0.90823 |  | N/A |  |  |  | N/A |  | z
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849533 | RXL09QMVJU | FTX09NMVJU | HRCU-A-CB-O | 12.5 | 20 | 12.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4446 | 10942 | 16036 | 0.23 | 0.761 | 1.701 | 5.67 | 4.21 | 2.76 |  | 2893 | 7121 | 12136 | 0.201 | 0.664 | 1.642 | 4.22 | 3.14 | 2.17 |  | 2262 |  | 10918 | 0.189 |  | 1.623 | 3.51 |  | 1.97 |  | 0.68084 | 0.89964 |  | N/A |  |  |  | N/A |  | z
Daikin AC (Americas), Inc | Daikin | Vista | 9966569 | RX09QMVJU | FFQ09Q2VJU | HRCU-A-CB-O | 11.7 | 20.9 | 13 | 9100 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) |  | 4600 | 10000 | 14000 | 0.25 | 0.64 | 1.15 | 5.4 | 4.59 | 3.57 |  | 3150 | 5830 | 8150 | 0.22 | 0.45 | 0.81 | 4.18 | 3.8 | 2.94 |  | 2420 |  | 6270 | 0.21 |  | 0.76 | 3.38 |  | 2.42 |  | 0.44786 | 0.76933 |  | accessory (KEH067A41E) | 140 | Temp below 23 degrees |  | N/A
Daikin AC (Americas), Inc | Daikin | Vista | 9966684 | RX12QMVJU | FFQ12Q2VJU | HRCU-A-CB-O | 11.2 | 20.2 | 12.5 | 10800 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) |  | 4600 | 13500 | 16800 | 0.25 | 0.99 | 1.45 | 5.4 | 4.02 | 3.39 |  | 3150 | 7850 | 9760 | 0.22 | 0.7 | 1.03 | 4.18 | 3.28 | 2.76 |  | 2420 |  | 7500 | 0.21 |  | 0.96 | 3.38 |  | 2.28 |  | 0.44643 | 0.76844 |  | accessory (KEH067A41E) | 140 | Temp. below 23 degrees |  | N/A
Daikin AC (Americas), Inc | Daikin | Vista | 9966775 | RX15QMVJU | FFQ15Q2VJU | HRCU-A-CB-O | 11 | 20.7 | 12.5 | 14400 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) |  | 5200 | 16200 | 16300 | 0.31 | 1.24 | 1.3 | 4.916 | 3.8288 | 3.6747 |  | 3570 | 9400 | 9460 | 0.27 | 0.87 | 0.92 | 3.8751 | 3.1665 | 3.0135 |  | 2740 |  | 7270 | 0.26 |  | 0.86 | 3.08 |  | 2.47 |  | 0.44601 | 0.7685 |  | accessory (KEH063A4E) | 140 | Temp below 23 degrees |  | N/A
Daikin AC (Americas), Inc | Daikin | Vista | 10318063 | RX18QMVJU | FFQ18Q2VJU | HRCU-A-CB-O | 10.1 | 19.3 | 12.5 | 17400 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) |  | 5400 | 21600 | 21800 | 0.37 | 1.88 | 1.92 | 4.2773 | 3.3672 | 3.3276 |  | 3640 | 12490 | 12610 | 0.33 | 1.33 | 1.36 | 3.24 | 2.74 | 2.72 |  | 2800 |  | 9700 | 0.31 |  | 1.27 | 2.6471 |  | 2.2384 |  | 0.44495 | 0.76923 |  | accessory (KEH063A4E) | 140 | Temp below 23 degrees |  | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8033584 | AOU18RLXFZH | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 21.5 | 13.5 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 6200 | 22000 | 24400 | 0.52 | 1.7 | 2.02 | 3.85 | 3.8 | 3.54 |  | 6619 | 14200 | 23500 | 0.81 | 1.6 | 3.18 | 2.4 | 2.6 | 2.16 |  | 6210 |  | 22000 | 0.89 |  | 3.49 | 2.04 |  | 1.85 |  | 0.90164 | 0.93617 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 3378 | z | 12000 | 0.55 |  | 2.14 | 1.8 |  | 1.64
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8033586 | AOU24RLXFZH | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 20 | 13.3 | 22000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 6200 | 25000 | 29800 | 0.5 | 1.81 | 2.85 | 4 | 4.04 | 3.06 |  | 6005 | 15400 | 26000 | 0.62 | 1.73 | 3.57 | 2.84 | 2.6 | 2.13 |  | 5869 |  | 25500 | 0.62 |  | 3.57 | 2.77 |  | 2.09 |  | 0.8557 | 0.98077 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 3207 | z | 13500 | 0.43 |  | 2.44 | 2.19 |  | 1.62
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8908615 | AOU36RLXFZH | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 20 | 13 | 35200 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 12000 | 36400 | 42000 | 0.7 | 2.67 | 3.29 | 5.02 | 4 | 3.74 |  | 11212 | 21400 | 39341 | 1.09 | 2.38 | 5.13 | 3.02 | 2.64 | 2.25 |  | 10376 |  | 36407 | 1.12 |  | 5.28 | 2.72 |  | 2.02 |  | 0.86683 | 0.92542 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 6301 | z | 22110 | 0.91 |  | 3.59 | 2.03 |  | 1.81
Fujitsu General America, Inc. | Fujitsu | J-Series | 8693477 | AOU48RLAVM | Non-Ducted Indoor Units | HMSV-A-CB | 11.4 | 19.8 | 12.5 | 4800 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 16630 | 54000 | 54000 | 0.91 | 4.06 | 4.06 | 5.3565 | 3.8981 | 3.8981 |  | 15400 | 33000 | 50000 | 1 | 3.4055 | 4.46 | 4.5134 | 2.84 | 3.2856 |  | 12720 |  | 41300 | 0.92288 |  | 4.12 | 4.0396 |  | 2.9379 |  | 0.76481 | 0.826 |  | N/A |  |  |  | -4 | 11240 |  | 36500 | 0.86016 |  | 3.84 | 3.8304 |  | 2.7858
Fujitsu General America, Inc. | Fujitsu | J-Series | 8693480 | AOU36RLAVM | Non-Ducted Indoor Units | HMSV-A-CB | 11.4 | 19 | 13.3 | 3600 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 16460 | 42000 | 42000 | 0.87 | 3.2 | 3.2 | 5.5462 | 3.8466 | 3.8466 |  | 16460 | 25800 | 42000 | 1.2 | 2.7005 | 4.43 | 4.021 | 2.8 | 2.7786 |  | 14860 |  | 37900 | 1.1043 |  | 4.06 | 3.9429 |  | 2.7359 |  | 0.90238 | 0.90238 |  | N/A |  |  |  | -4 | 13170 |  | 33600 | 1.02 |  | 3.75 | 3.7845 |  | 2.626
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RL2 Series | 5063325 | AOU9RLS2 | ASU9RLS2 | HRCU-A-CB-O | 12.5 | 27.2 | 16.1 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 12000 | 22000 | 0.2 | 0.8 | 1.99 | 4.5 | 4.4 | 3.24 |  | 2320 | 9400 | 16400 | 0.2 | 1.09 | 1.97 | 3.4 | 2.54 | 2.45 |  | 2150 |  | 15000 | 0.21 |  | 2.06 | 3 |  | 2.18 |  | 0.68182 | 0.91463 |  | N/A |  |  |  | -5 | 1945 | z | 13500 | 0.21 |  | 2.05 | 2.71 |  | 2
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RL2 Series | 5063326 | AOU12RLS2 | ASU12RLS2 | HRCU-A-CB-O | 12 | 25 | 13.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 22110 | 0.2 | 1.2 | 2 | 4.5 | 3.91 | 3.24 |  | 2491 | 10200 | 17900 | 0.2 | 1.1 | 2 | 3.65 | 2.72 | 2.63 |  | 2320 |  | 16500 | 0.21 |  | 2.1 | 3.24 |  | 2.34 |  | 0.74627 | 0.92179 |  | N/A |  |  |  | -5 | 2081 | z | 15000 | 0.21 |  | 2.1 | 2.9 |  | 2.1
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Compact Cassette | 5751311 | AOU9RLFC | AUU9RLF | HRCU-A-CB-O | 13 | 24 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 12000 | 18000 | 0.15 | 0.89 | 1.8 | 6 | 3.95 | 2.93 |  | 2744 | 9400 | 16100 | 0.14 | 0.96 | 1.78 | 5.65 | 2.88 | 2.66 |  | 2610 |  | 15000 | 0.15 |  | 1.87 | 5.11 |  | 2.41 |  | 0.83333 | 0.93168 |  | N/A |  |  |  | -5 | 2378 | z | 13500 | 0.15 |  | 1.92 | 4.54 |  | 2.14
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Slim Duct | 5751312 | AOU9RLFC | ARU9RLF | HRCU-A-CB-O | 12.2 | 21.5 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 12000 | 18000 | 0.15 | 0.85 | 1.8 | 6 | 4.14 | 2.93 |  | 2744 | 9400 | 16100 | 0.14 | 0.96 | 1.78 | 5.65 | 2.88 | 2.66 |  | 2610 |  | 15000 | 0.15 |  | 1.87 | 5.11 |  | 2.41 |  | 0.83333 | 0.93168 |  | N/A |  |  |  | -5 | 2378 | z | 13500 | 0.15 |  | 1.92 | 4.54 |  | 2.14
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Compact Cassette | 5751313 | AOU12RLFC | AUU12RLF | HRCU-A-CB-O | 12.2 | 21.9 | 12.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 19400 | 0.15 | 1.44 | 2 | 6 | 3.26 | 2.85 |  | 2793 | 10200 | 17600 | 0.17 | 1.16 | 2.15 | 4.76 | 2.58 | 2.41 |  | 2647 |  | 16500 | 0.18 |  | 2.25 | 4.31 |  | 2.18 |  | 0.85052 | 0.9375 |  | N/A |  |  |  | -5 | 2377 | z | 15000 | 0.19 |  | 2.32 | 3.75 |  | 1.9
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Slim Duct | 5751314 | AOU12RLFC | ARU12RLF | HRCU-A-CB-O | 11.5 | 20 | 12.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 19400 | 0.15 | 1.3 | 2 | 6 | 3.61 | 2.85 |  | 2793 | 10200 | 17600 | 0.17 | 1.16 | 2.15 | 4.76 | 2.58 | 2.41 |  | 2647 |  | 16500 | 0.18 |  | 2.25 | 4.31 |  | 2.18 |  | 0.85052 | 0.9375 |  | N/A |  |  |  | -5 | 2377 | z | 15000 | 0.19 |  | 2.32 | 3.75 |  | 1.9
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFFH Series | 6936995 | AOU9RLFF | AGU9RLF | HRCU-A-CB-O | 12.6 | 26 | 16 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 12000 | 18800 | 0.2 | 0.88 | 1.84 | 4.5428 | 3.9966 | 2.99 |  | 2320 | 7500 | 14000 | 0.2 | 0.78 | 1.82 | 3.4 | 2.8 | 2.25 |  | 2115 |  | 14000 | 0.19 |  | 2.1 | 3.26 |  | 1.95 |  | 0.74468 | 1 |  | N/A |  |  |  | -5 | 2047 | z | 12500 | 0.22 |  | 2 | 2.73 |  | 1.83
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFFH Series | 6936996 | AOU12RLFF | AGU12RLF | HRCU-A-CB-O | 11.6 | 22.7 | 13.1 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 19500 | 0.2 | 1.44 | 1.84 | 4.5428 | 3.2565 | 3.1 |  | 2457 | 10600 | 15000 | 0.24 | 1.19 | 2.17 | 3 | 2.6 | 2.02 |  | 2423 |  | 15000 | 0.24 |  | 2.17 | 2.96 |  | 2.02 |  | 0.76923 | 1 |  | N/A |  |  |  | -5 | 2115 | z | 13000 | 0.22 |  | 2.06 | 2.82 |  | 1.85
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFFH Series | 6936997 | AOU15RLFF | AGU15RLF | HRCU-A-CB-O | 11.2 | 20.3 | 12.5 | 14200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 18000 | 20800 | 0.18 | 1.58 | 2.01 | 5.0475 | 3.3389 | 3.03 |  | 2832 | 11600 | 19000 | 0.32 | 1.3 | 2.89 | 2.59 | 2.62 | 1.93 |  | 2798 |  | 18500 | 0.26 |  | 2.91 | 3.15 |  | 1.86 |  | 0.88942 | 0.97368 |  | N/A |  |  |  | -5 | 2593 | z | 17500 | 0.26 |  | 2.86 | 2.92 |  | 1.79
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFF Series | 6937309 | AOU9RLFFH | AGU9RLF | HRCU-A-CB-O | 12.4 | 26 | 16 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 12000 | 18800 | 0.2 | 0.88 | 1.84 | 4.5428 | 3.9966 | 2.99 |  | 2320 | 7500 | 14000 | 0.35 | 0.78 | 1.97 | 1.94 | 2.8 | 2.08 |  | 2115 |  | 14000 | 0.34 |  | 2.25 | 1.82 |  | 1.82 |  | 0.74468 | 1 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 1843 | z | 11000 | 0.38 |  | 2.07 | 1.42 |  | 1.56
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFF Series | 6937310 | AOU12RLFFH | AGU12RLF | HRCU-A-CB-O | 11.3 | 22.7 | 13.1 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 19500 | 0.2 | 1.44 | 1.84 | 4.5428 | 3.2565 | 3.1 |  | 2457 | 10600 | 15000 | 0.39 | 1.19 | 2.32 | 1.85 | 2.6 | 1.89 |  | 2423 |  | 15000 | 0.39 |  | 2.32 | 1.82 |  | 1.89 |  | 0.76923 | 1 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 2252 | z | 14000 | 0.48 |  | 2.99 | 1.38 |  | 1.37
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFF Series | 6937311 | AOU15RLFFH | AGU15RLF | HRCU-A-CB-O | 11 | 20.3 | 12.5 | 14200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 18000 | 20800 | 0.18 | 1.58 | 2.01 | 5.0475 | 3.3389 | 3.03 |  | 2832 | 11600 | 19000 | 0.47 | 1.3 | 3.04 | 1.77 | 2.62 | 1.83 |  | 2798 |  | 18500 | 0.41 |  | 3.06 | 2 |  | 1.77 |  | 0.88942 | 0.97368 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 2320 | z | 15500 | 0.41 |  | 2.93 | 1.66 |  | 1.55
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 7993242 | AOU12RLS3 | ASU12RLS3 | HRCU-A-CB-O | 14 | 29.3 | 15.2 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5428 | 4.6429 | 3.34 |  | 2491 | 9600 | 17500 | 0.21 | 0.85 | 2.06 | 3.48 | 3.3 | 2.49 |  | 2320 |  | 16500 | 0.22 |  | 2.1 | 3.09 |  | 2.3 |  | 0.74627 | 0.94286 |  | N/A |  |  |  | -5 | 2081 | z | 15000 | 0.22 |  | 2.09 | 2.77 |  | 2.1
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 7993243 | AOU15RLS3 | ASU15RLS3 | HRCU-A-CB-O | 13.4 | 25.3 | 13.9 | 14500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.29 | 4.5874 | 3.2 |  | 2798 | 11200 | 21500 | 0.2 | 1.04 | 2.59 | 4.1 | 3.14 | 2.43 |  | 2696 |  | 20500 | 0.21 |  | 2.75 | 3.76 |  | 2.18 |  | 0.85774 | 0.95349 |  | N/A |  |  |  | -5 | 2388 | z | 18500 | 0.21 |  | 2.74 | 3.33 |  | 1.98
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 7993244 | AOU12RLS3H | ASU12RLS3 | HRCU-A-CB-O | 13.8 | 29.3 | 15.2 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5 | 4.6429 | 3.34 |  | 2491 | 9600 | 17500 | 0.36 | 0.88 | 2.21 | 2.03 | 3.18 | 2.32 |  | 2320 |  | 16500 | 0.37 |  | 2.25 | 1.84 |  | 2.15 |  | 0.74627 | 0.94286 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 1638 | z | 11500 | 0.38 |  | 2.23 | 1.26 |  | 1.51
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 7993245 | AOU15RLS3H | ASU15RLS3 | HRCU-A-CB-O | 13.3 | 25.3 | 13.9 | 14500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.29 | 4.5874 | 3.2 |  | 2798 | 11200 | 21500 | 0.35 | 1.07 | 2.74 | 2.34 | 3.06 | 2.3 |  | 2696 |  | 20500 | 0.36 |  | 2.9 | 2.19 |  | 2.07 |  | 0.85774 | 0.95349 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 2081 | z | 16000 | 0.37 |  | 2.88 | 1.65 |  | 1.63
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 8004699 | AOU9RLS3 | ASU9RLS3 | HRCU-A-CB-O | 14.2 | 33 | 18 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5 | 5.3288 | 3.34 |  | 2286 | 7000 | 16000 | 0.21 | 0.59 | 2.06 | 3.19 | 3.46 | 2.28 |  | 2150 |  | 15000 | 0.22 |  | 2.1 | 2.86 |  | 2.09 |  | 0.68182 | 0.9375 |  | N/A |  |  |  | -5 | 1945 | z | 13500 | 0.22 |  | 2.09 | 2.59 |  | 1.89
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 8004700 | AOU9RLS3H | ASU9RLS3 | HRCU-A-CB-O | 14 | 33 | 18 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5 | 5.3288 | 3.34 |  | 2286 | 7000 | 16000 | 0.36 | 0.61 | 2.21 | 1.86 | 3.36 | 2.12 |  | 2150 |  | 15000 | 0.37 |  | 2.25 | 1.7 |  | 1.95 |  | 0.68182 | 0.9375 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 1535 | z | 11000 | 0.38 |  | 2.23 | 1.18 |  | 1.44
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall mounted RLS3 Series | 8703348 | AOU9RLS3 | ASU9RLS3Y | HRCU-A-CB-O | 14.2 | 33 | 18 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5426 | 5.3288 | 3.34 |  | 2286 | 7000 | 16000 | 0.21 | 0.59 | 2.06 | 3.19 | 3.46 | 2.28 |  | 2150 |  | 15000 | 0.22 |  | 2.1 | 2.86 |  | 2.09 |  | 0.68182 | 0.9375 |  | N/A |  |  |  | -5 | 1945 | z | 13500 | 0.22 |  | 2.09 | 2.59 |  | 1.89
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall mounted H Series | 8703349 | AOU9RLS3H | ASU9RLS3Y | HRCU-A-CB-O | 14 | 33 | 18 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5426 | 5.33 | 3.34 |  | 2286 | 7000 | 16000 | 0.36 | 0.61 | 2.21 | 1.86 | 3.36 | 2.12 |  | 2150 |  | 15000 | 0.37 |  | 2.25 | 1.7 |  | 1.95 |  | 0.68182 | 0.9375 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 1535 | z | 11000 | 0.38 |  | 2.23 | 1.18 |  | 1.44
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 8703350 | AOU12RLS3 | ASU12RLS3Y | HRCU-A-CB-O | 14 | 29.3 | 15.2 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5426 | 4.64 | 3.34 |  | 2491 | 9600 | 17500 | 0.21 | 0.85 | 2.06 | 3.48 | 3.3 | 2.49 |  | 2320 |  | 16500 | 0.22 |  | 2.1 | 3.09 |  | 2.3 |  | 0.74627 | 0.94286 |  | N/A |  |  |  | -5 | 2081 | z | 15000 | 0.22 |  | 2.09 | 2.77 |  | 2.1
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3H Series | 8703506 | AOU12RLS3H | ASU12RLS3Y | HRCU-A-CB-O | 13.8 | 29.3 | 15.2 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5426 | 4.64 | 3.34 |  | 2491 | 9600 | 17500 | 0.36 | 0.88 | 2.21 | 2.03 | 3.18 | 2.32 |  | 2320 |  | 16500 | 0.37 |  | 2.25 | 1.84 |  | 2.15 |  | 0.74627 | 0.94286 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 1638 | z | 11500 | 0.38 |  | 2.23 | 1.26 |  | 1.51
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall mounted RLS3 Series | 8703507 | AOU15RLS3 | ASU15RLS3Y | HRCU-A-CB-O | 13.4 | 25.3 | 13.9 | 14500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.3442 | 4.59 | 3.2 |  | 2798 | 11200 | 21500 | 0.2 | 1.04 | 2.59 | 4.1 | 3.14 | 2.43 |  | 2696 |  | 20500 | 0.21 |  | 2.75 | 3.76 |  | 2.18 |  | 0.85774 | 0.95349 |  | N/A |  |  |  | -5 | 2388 | z | 18500 | 0.21 |  | 2.74 | 3.33 |  | 1.98
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 8703508 | AOU15RLS3H | ASU15RLS3Y | HRCU-A-CB-O | 13.3 | 25.3 | 13.9 | 14500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.3442 | 4.59 | 3.2 |  | 2798 | 11200 | 21500 | 0.35 | 1.07 | 2.74 | 2.34 | 3.06 | 2.3 |  | 2696 |  | 20500 | 0.36 |  | 2.9 | 2.19 |  | 2.07 |  | 0.85774 | 0.95349 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 2081 | z | 16000 | 0.37 |  | 2.88 | 1.65 |  | 1.63
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF/RLX Series | 8718495 | AOU18RLXFW1 | ASU18RLF | HRCU-A-CB-O | 10.5 | 20 | 13.3 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 7000 | 21600 | 29000 | 0.48 | 1.75 | 2.99 | 4.27 | 3.62 | 2.84 |  | 5485 | 14600 | 22759 | 0.42 | 1.39 | 2.85 | 3.83 | 3.08 | 2.34 |  | 5205 |  | 21600 | 0.39 |  | 2.6 | 3.91 |  | 2.43 |  | 0.74483 | 0.94908 |  | N/A |  |  |  | -5 | 4745 | z | 19688 | 0.33 |  | 2.22 | 4.21 |  | 2.6
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF/RLX Series | 8779045 | AOU18RLXFWH | ASU18RLF | HRCU-A-CB-O | 10.4 | 20 | 13.3 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 7000 | 21600 | 29000 | 0.48 | 1.75 | 2.99 | 4.27 | 3.62 | 2.84 |  | 5485 | 14600 | 22759 | 0.57 | 1.42 | 3 | 2.82 | 3.02 | 2.22 |  | 5205 |  | 21600 | 0.54 |  | 2.75 | 2.82 |  | 2.3 |  | 0.74483 | 0.94908 |  | Integrated | 150 | Operation depends on outdoor temperature & demand |  | -15 | 4317 | z | 17913 | 0.42 |  | 1.83 | 3.01 |  | 2.87
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8779046 | AOU24RLXFWH | ASU24RLF | HRCU-A-CB-O | 10.5 | 19.5 | 12.5 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 7500 | 21850 | 36200 | 0.5 | 1.94 | 3.38 | 4.4 | 3.3 | 3.14 |  | 5740 | 16720 | 27700 | 0.64 | 2.11 | 3.59 | 2.63 | 2.32 | 2.26 |  | 5220 |  | 25220 | 0.64 |  | 3.59 | 2.4 |  | 2.06 |  | 0.69669 | 0.91047 |  | Integrated | 0.15 | Cold outside & demand |  | -15 | 7510 |  | 19720 | 0.5 |  | 3.22 | 4.4 |  | 1.8
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8912454 | AOU30RLXEH | ASU30RLE | HRCU-A-CB-O | 11.8 | 18.7 | 12.5 | 30000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 8000 | 22600 | 37200 | 0.5 | 2.4 | 2.54 | 4.7 | 2.77 | 2.54 |  | 7570 | 21400 | 35200 | 0.53 | 2.52 | 4.51 | 4.2 | 2.49 | 2.29 |  | 6890 |  | 32040 | 0.53 |  | 4.55 | 3.79 |  | 2.06 |  | 0.86129 | 0.91023 |  | Integrated | 0.15 | Cold outside & demand |  | -15 | 4620 |  | 22860 | 0.46 |  | 3.95 | 3.12 |  | 1.7
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF Series | 6961728 | AOU9RLFW1 | ASU9RLF1 | HRCU-A-CB-O | 11 | 23 | 13.8 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 1700 | 12000 | 15000 | 0.25 | 0.89 | 1.6 | 2 | 3.95 | 2.75 |  | 1079 | 7600 | 9500 | 0.2 | 0.71 | 1.27 | 1.59 | 3.1363 | 2.1917 |  | 969 |  | 8530 | 0.19944 |  | 1.27 | 1.4236 |  | 1.9679 |  | 0.56867 | 0.89789 |  | N/A |  |  |  | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF Series | 6961729 | AOU12RLFW1 | ASU12RLF1 | HRCU-A-CB-O | 11 | 22 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 16000 | 19100 | 0.25 | 1.28 | 1.99 | 3.6 | 3.66 | 2.8122 |  | 1795 | 9400 | 11200 | 0.19 | 0.96 | 1.4925 | 2.8 | 2.869 | 2.196 |  | 1949 |  | 12150 | 0.22266 |  | 1.7723 | 2.57 |  | 2.0071 |  | 0.63613 | 1.0848 |  | N/A |  |  |  | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLB Series | 7937663 | AOU18RLB | ASU18RLB | HRCU-A-CB-O | 10.6 | 19 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3100 | 18000 | 20000 | 0.17 | 1.285 | 2.06 | 5.29 | 4.11 | 2.8447 |  | 2798 | 11500 | 16700 | 0.2 | 1.15 | 2.1 | 4.0991 | 2.92 | 2.3327 |  | 2696 |  | 15400 | 0.21 |  | 2.18 | 3.76 |  | 2.0698 |  | 0.77 | 0.92216 |  | N/A |  |  |  | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8718545 | AOU24RLXFW1 | ASU24RLF | HRCU-A-CB-O | 10.6 | 19.5 | 12.5 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 7500 | 21850 | 36200 | 0.5 | 1.94 | 3.38 | 4.4 | 3.3 | 3.14 |  | 5740 | 16720 | 27700 | 0.49 | 1.96 | 3.44 | 3.44 | 2.49 | 2.36 |  | 5220 |  | 25220 | 0.49 |  | 3.44 | 3.13 |  | 2.15 |  | 0.69669 | 0.91047 |  | N/A |  |  |  | -5 | 4670 |  | 22550 | 0.47 |  | 3.28 | 2.94 |  | 2.02
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7434477 | MXZ-5C42NAHZ | Non-Ducted Indoor Units | HMSV-A-CB | 11 | 19 | 13.4 | 42000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 24000 | 48000 | 48000 | 1.17 | 3.43 | 3.43 | 6.01 | 4.1 | 4.1 |  | 24000 | 35800 | 48000 | 1.66 | 3.65 | 4.87 | 4.23 | 2.87 | 2.89 |  | 24000 |  | 48000 | 1.91 |  | 5.61 | 3.69 |  | 2.51 |  | 1 | 1 |  | Integrated | 150W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes |  | -13 | 24000 | z | 36000 | 2.5 |  | 4.8 | 2.81 |  | 2.2
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7434482 | MXZ-4C36NAHZ | Non-Ducted Indoor Units | HMSV-A-CB | 11.3 | 19.1 | 14 | 36000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 22500 | 45000 | 45000 | 1.09 | 3.34 | 3.34 | 6.05 | 3.95 | 3.95 |  | 22500 | 34000 | 45000 | 1.55 | 3.5 | 4.74 | 4.26 | 2.85 | 2.78 |  | 22500 |  | 45000 | 1.78 |  | 5.46 | 3.71 |  | 2.41 |  | 1 | 1 |  | Integrated | 150W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes |  | -13 | 22500 | z | 33800 | 2.33 |  | 4.68 | 2.83 |  | 2.12
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7434486 | MXZ-4C36NAHZ | Mixed | HMSV-A-CB | 10.7 | 17.45 | 12.65 | 36000 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units |  | 22500 | 45000 | 45000 | 1.3 | 3.8 | 3.8 | 5.07 | 3.48 | 3.48 |  | 22500 | 35000 | 45000 | 2.15 | 4.05 | 5.35 | 3.07 | 2.54 | 2.47 |  | 22500 |  | 45000 | 2.62 |  | 6.21 | 2.52 |  | 2.16 |  | 1 | 1 |  | N/A |  |  |  | -13 | 22500 | z | 33800 | 3.14 |  | 5.32 | 2.1 |  | 1.89
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10091325 | MXZ-2C20NA2 | Non-ducted | HMSV-A-CB | 10 | 20 | 12.7 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 7400 | 22000 | 25500 | 0.67 | 1.641 | 2.455 | 3.2369 | 3.929 | 3.0441 |  | 12500 | 12500 | 15500 | 1.5 | 1.3 | 1.75 | 2.4423 | 2.818 | 2.5958 |  | 10500 |  | 11100 | 1 |  | 1.6 | 3.0772 |  | 2.0332 |  | 0.43529 | 0.66667 |  | MAC-646BH-E | 120 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953943 | PUMY-P36NKMU1 | Non-ducted | HMSV-A-CB | 11.5 | 21 | 14.2 | 36000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 13313 | 42000 | 42000 | 0.62 | 3.16 | 3.16 | 6.293 | 3.8952 | 3.8952 |  | 9690 | 26400 | 35000 | 0.726 | 2.59 | 3.799 | 3.9117 | 2.9873 | 2.7 |  | 6687 |  | 29000 | 0.582 |  | 3.695 | 3.3673 |  | 2.3002 |  | 0.69048 | 0.80165 |  | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953946 | PUMY-P48NKMU1 | Non-ducted | HMSV-A-CB | 11.7 | 20.2 | 12.6 | 48000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 15976 | 54000 | 54000 | 0.784 | 4.165 | 4.165 | 5.9721 | 3.7997 | 3.7997 |  | 11628 | 31400 | 43000 | 0.917 | 3.15 | 5.041 | 3.7163 | 2.9214 | 2.4999 |  | 8025 |  | 36400 | 0.735 |  | 4.849 | 3.1999 |  | 2.2 |  | 0.67407 | 0.80153 |  | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953947 | PUMY-P60NKMU1 | Non-ducted | HMSV-A-CB | 11.4 | 18.6 | 12.5 | 60000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 19526 | 66000 | 66000 | 1.027 | 5.53 | 5.53 | 5.5721 | 3.4978 | 3.4978 |  | 14121 | 41500 | 65000 | 1.201 | 4.68 | 8.283 | 3.446 | 2.5988 | 2.2998 |  | 9809 |  | 57000 | 0.963 |  | 8.353 | 2.9852 |  | 1.9999 |  | 0.86364 | 0.80183 |  | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 9141022 | PUMY-P36NKMU1 | Mixed | HMSV-A-CB | 11 | 18.3 | 13.4 | 36000 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units |  | 13313 | 42000 | 42000 | 0.646 | 3.29 | 3.29 | 6.0397 | 3.7413 | 3.7413 |  | 9690 | 26500 | 35500 | 0.783 | 2.794 | 3.95 | 3.627 | 2.7797 | 2.6339 |  | 6687 |  | 29000 | 0.606 |  | 3.798 | 3.2339 |  | 2.2378 |  | 0.69048 | 0.77395 |  | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 9722847 | MXZ-8C60NA | Non-ducted | HMSV-A-CB | 10.5 | 17.4 | 12.5 | 60000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 19526 | 66000 | 66000 | 1.053 | 1.053 | 1.053 | 5.4345 | 3.4114 | 3.4114 |  | 14212 | 41500 | 65000 | 1.232 | 4.87 | 9.525 | 3.3809 | 2.4974 | 2 |  | 9808 |  | 57000 | 0.987 |  | 8.1 | 2.9123 |  | 2.0624 |  | 0.86364 | 0.80114 |  | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 8993522 | MXZ-3C30NAHZ2 | Non-Ducted Indoor Units | HMSV-A-CB | 11 | 18 | 12.5 | 28400 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 11400 | 28600 | 28600 | 0.93 | 2.1 | 2.1 | 3.59 | 4 | 4 |  | 13100 | 18000 | 28600 | 1.5 | 1.99 | 4.19 | 2.5596 | 2.65 | 2 |  | 12500 |  | 28600 | 1.6 |  | 4.79 | 2.29 |  | 1.75 |  | 1 | 1 |  | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes |  | -13 | 10000 | z | 25225 | 1.4 |  | 4.49 | 2.09 |  | 1.64
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 8996108 | MXZ-3C24NAHZ2 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 19 | 13.5 | 22000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 11400 | 25000 | 25000 | 0.93 | 1.72 | 1.72 | 3.59 | 4.25 | 4.25 |  | 13100 | 14000 | 25000 | 1.5 | 1.62 | 3.56 | 2.5596 | 2.53 | 2.06 |  | 12500 |  | 25000 | 1.6 |  | 3.82 | 2.29 |  | 1.92 |  | 1 | 1 |  | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes |  | -13 | 10000 | z | 22050 | 1.4 |  | 3.52 | 2.09 |  | 1.83
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953944 | PUMY-P36NKMU1 | Ducted indoor units | HMSV-A-CB | 10.5 | 15.6 | 12.6 | 36000 | Yes | Ductless | Multi-zone | Ducted Indoor Units |  | 13313 | 42000 | 42000 | 0.671 | 3.42 | 3.42 | 5.8147 | 3.5991 | 3.5991 |  | 9690 | 26600 | 36000 | 0.84 | 2.998 | 4.1 | 3.3809 | 2.6003 | 2.5733 |  | 6687 |  | 30000 | 0.63 |  | 3.9 | 3.1107 |  | 2.2544 |  | 0.71429 | 0.75 |  | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7451794 | MXZ-3C30NAHZ | Non-Ducted Indoor Units | N/A | 11 | 18 | 12.5 |  | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) |  | 11400 | 28600 | 28600 | 0.93 | 2.1 | 2.1 | 3.59 | 4 | 4 |  | 13100 | 18000 | 28600 | 1.5 | 1.99 | 4.19 | 2.5596 | 2.65 | 2 |  | 12500 |  | 28600 | 1.6 |  | 4.79 | 2.29 |  | 1.75 |  | 1 | 1 |  | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes |  | -13 | 10000 | z | 25225 | 1.4 |  | 4.49 | 2.09 |  | 1.64
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 7451969 | MXZ-3C24NAHZ | Non-Ducted Indoor Units | N/A | 10 | 19 | 13.5 |  | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) |  | 11400 | 25000 | 25000 | 0.93 | 1.72 | 1.72 | 3.59 | 4.25 | 4.25 |  | 13100 | 14000 | 25000 | 1.5 | 1.62 | 3.56 | 2.5596 | 2.53 | 2.06 |  | 12500 |  | 25000 | 1.6 |  | 3.82 | 2.29 |  | 1.92 |  | 1 | 1 |  | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes |  | -13 | 10000 | z | 22050 | 1.4 |  | 3.52 | 2.09 |  | 1.83
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 3837467 | SUZ-KA12NA | SEZ-KD12NA | HRCU-A-CB | 10 | 16 | 12.5 | 11500 | Yes | Ductless | Single-zone | Ducted Indoor Units |  | 4800 | 13600 | 16400 | 0.34 | 1.14 | 1.52 | 4.1375 | 3.4963 | 3.1621 |  | 3100 | 9000 | 10800 | 0.36 | 0.92 | 1.2 | 2.5237 | 2.867 | 2.6376 |  | 2199 |  | 7400 | 0.27 |  | 0.9 | 2.3869 |  | 2.4097 |  | 0.45122 | 0.75 |  | N/A |  |  |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 3837470 | SUZ-KA18NA | SEZ-KD18NA | HRCU-A-CB | 10 | 17.5 | 12.5 | 17200 | Yes | Ductless | Single-zone | Ducted Indoor Units |  | 4800 | 21600 | 24900 | 0.26 | 1.7 | 2.15 | 5.4105 | 3.7237 | 3.3942 |  | 2900 | 13100 | 15000 | 0.31 | 1.35 | 1.8 | 2.7416 | 2.8439 | 2.4423 |  | 1900 |  | 9900 | 0.23 |  | 1.32 | 2.421 |  | 2.198 |  | 0.39759 | 0.74194 |  | N/A |  |  |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | P-Series | 8635969 | PUZ-HA36NHA5 | PVA-A36AA4 | HRCU-A-CB-O | 11 | 17.8 | 12.5 | 33000 | Yes | Centrally Ducted | N/A | N/A |  | 18000 | 38000 | 40000 | 1.14 | 3.04 | 3.36 | 4.63 | 3.66 | 3.49 |  | 19000 | 25000 | 38000 | 2.03 | 3.33 | 5.4 | 2.74 | 2.2 | 2.06 |  | 15000 |  | 38000 | 1.73 |  | 6.1 | 2.54 |  | 1.82 |  | 0.95 | 1 |  | N/A |  |  |  | -13 | 13000 | z | 29000 | 1.77 |  | 6.15 | 2.15 |  | 1.38
Mitsubishi Electric Cooling & Heating | Mitsubishi | P-Series Hyper Heat | 8635970 | PUZ-HA36NHA5 | PEAD-A36AA* | HRCU-A-CB-O | 10.4 | 16.8 | 12.5 | 33000 | Yes | Centrally Ducted | N/A | N/A |  | 18000 | 38000 | 40000 | 1.16 | 3.15 | 3.27 | 4.54 | 3.53 | 3.58 |  | 14000 | 27000 | 38000 | 1.54 | 3.25 | 5.4 | 2.66 | 2.43 | 2.06 |  | 10000 |  | 38000 | 1.21 |  | 6.1 | 2.42 |  | 1.82 |  | 0.95 | 1 |  | Integrated | 120W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32°F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2°F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | P-Series Hyper Heat | 8635971 | PUZ-HA36NHA5 | PLA-A36BA* | HRCU-A-CB-O | 10 | 17 | 12.6 | 34000 | Yes | Ductless | Single-zone | Non-ducted indoor Unit (Ceiling Cassette) |  | 18000 | 38000 | 40000 | 1.19 | 3.13 | 3.75 | 4.43 | 3.55 | 3.14 |  | 14000 | 28000 | 38000 | 1.38 | 3.59 | 5.3 | 2.97 | 2.28 | 2.12 |  | 9000 |  | 38000 | 0.97 |  | 5.79 | 2.71 |  | 1.92 |  | 0.95 | 1 |  | Integrated | 120W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32°F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2°F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715786 | MUZ-GL24NA-U1 | MSZ-GL24NA-U1 | HRCU-A-CB-O | 10 | 20.5 | 12.5 | 22400 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 7500 | 27600 | 36900 | 0.52 | 2.34 | 3.65 | 4.227 | 3.4567 | 2.9628 |  | 4900 | 16000 | 24600 | 0.72 | 1.77 | 3.29 | 1.9945 | 2.6492 | 2.1914 |  | 4380 |  | 20200 | 0.64 |  | 2.99 | 2.0057 |  | 1.9799 |  | 0.54743 | 0.88889 |  | MAC-642BH-U1 | 120 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 4908219 | MUZ-FE09NA | MSZ-FE09NA | HRCU-A-CB-O | 10 | 26 | 15.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3000 | 10900 | 18000 | 0.15 | 0.71 | 2.25 | 5.8617 | 4.5 | 2.34 |  | 1700 | 6700 | 12500 | 0.11 | 0.65 | 1.73 | 4.53 | 3.02 | 2.12 |  | 1200 |  | 10900 | 0.08 |  | 1.46 | 4.4 |  | 2.19 |  | 0.60556 | 0.872 |  | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A |  | z
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 4934170 | MUZ-FE12NA | MSZ-FE12NA | HRCU-A-CB-O | 10.5 | 23 | 12.9 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3000 | 13600 | 21000 | 0.15 | 0.95 | 2.25 | 5.8617 | 4.2 | 2.74 |  | 1700 | 8300 | 13600 | 0.11 | 0.8 | 1.78 | 4.53 | 3.04 | 2.24 |  | 1200 |  | 13600 | 0.08 |  | 1.62 | 4.4 |  | 2.46 |  | 0.64762 | 1 |  | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A |  | z
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7002062 | MUZ-FH09NA | MSZ-FH09NA | HRCU-A-CB-O | 13.5 | 30.5 | 16.1 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 1600 | 10900 | 18000 | 0.11 | 0.71 | 1.47 | 4.263 | 4.5 | 3.59 |  | 920 | 6700 | 12200 | 0.08 | 0.6 | 1.44 | 3.37 | 3.27 | 2.48 |  | 640 |  | 10900 | 0.06 |  | 1.35 | 3.13 |  | 2.32 |  | 0.60556 | 0.89344 |  | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | -13 | 240 | z | 7300 | 0.03 |  | 1.25 | 2.34 |  | 1.71
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7002063 | MUZ-FH12NA | MSZ-FH12NA | HRCU-A-CB-O | 12.5 | 26.1 | 13.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3700 | 13600 | 21000 | 0.28 | 0.95 | 2.3 | 3.8729 | 4.2 | 2.68 |  | 2100 | 8000 | 13600 | 0.2 | 0.72 | 1.9 | 3.08 | 3.26 | 2.1 |  | 1450 |  | 13600 | 0.15 |  | 1.8 | 2.83 |  | 2.21 |  | 0.64762 | 1 |  | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | -13 | 550 | z | 9900 | 0.07 |  | 1.6 | 2.3 |  | 1.81
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 7002444 | MUZ-FH15NA | MSZ-FH15NA | HRCU-A-CB-O | 12 | 22 | 12.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 5150 | 18000 | 24000 | 0.43 | 1.3 | 3.36 | 3.5102 | 4.06 | 2.09 |  | 2950 | 11000 | 18000 | 0.31 | 1.02 | 2.48 | 2.79 | 3.16 | 2.13 |  | 2050 |  | 18000 | 0.23 |  | 2.95 | 2.61 |  | 1.79 |  | 0.75 | 1 |  | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | -13 | 750 | z | 14600 | 0.11 |  | 2.35 | 2 |  | 1.82
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr.Slim FH Series | 8703451 | MUZ-FH12NAH | MSZ-FH12NAH | HRCU-A-CB-O | 11.5 | 26.1 | 13.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3700 | 13600 | 21000 | 0.28 | 0.95 | 2.3 | 3.8729 | 4.2 | 2.68 |  | 2100 | 8100 | 13600 | 0.33 | 0.84 | 1.96 | 1.87 | 2.83 | 1.96 |  | 1450 |  | 13600 | 0.28 |  | 1.93 | 1.52 |  | 2.07 |  | 0.64762 | 1 |  | Integrated | 106W @208V; 130W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A | 550 |  | 9900 | 0.2 |  | 1.73 | 0.81 |  | 1.68
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr.Slim FH Series | 8737963 | MUZ-FH09NAH | MSZ-FH09NAH | HRCU-A-CB-O | 12.5 | 30.5 | 16.1 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 1600 | 10900 | 18000 | 0.11 | 0.55 | 1.27 | 4.263 | 5.86 | 4.15 |  | 920 | 6700 | 12200 | 0.34 | 0.72 | 1.26 | 0.79 | 2.73 | 2.84 |  | 640 |  | 10900 | 0.32 |  | 1.17 | 0.59 |  | 2.73 |  | 0.60556 | 0.89344 |  | Integrated | 106W @208V; 130W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A | 240 |  | 7300 | 0.29 |  | 1.06 | 0.24 |  | 2.02
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8737964 | MUZ-FH15NAH | MSZ-FH15NA | HRCU-A-CB-O | 11 | 22 | 12.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) |  | 4280 | 18540 | 24200 | 0.61 | 1.33 | 3.4 | 2.0564 | 4.0854 | 2.086 | 3570 | 3570 | 11070 | 20200 | 0.6 | 0.95 | 3.36 | 1.7438 | 3.415 | 1.7619 | 3240 | 3240 | 8550 | 18300 | 0.55 | 0.74 | 2.98 | 1.7265 | 3.3862 | 1.7997 |  | 0.7562 | 0.91667 |  | Integrated | 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | -13 | 2610 |  | 14700 | 0.56 |  | 2.54 | 1.3659 |  | 1.6961
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8737968 | MUZ-FE09NAH | MSZ-FE09NA | HRCU-A-CB-O | 10 | 26 | 15.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) |  | 3000 | 10900 | 18000 | 0.15 | 0.71 | 2.25 | 5.8614 | 4.4993 | 2.3446 | 1840 | 1840 | 6700 | 13700 | 0.26 | 0.67 | 1.89 | 2.074 | 2.9307 | 2.1244 | 1430 | 1430 | 11200 | 11200 | 0.25 | 1.59 | 1.59 | 1.6764 | 2.0644 | 2.7709 |  | 0.62222 | 0.81752 |  | Integrated | 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8737969 | MUZ-FE12NAH | MSZ-FE12NA | HRCU-A-CB-O | 10.1 | 23 | 12.9 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) |  | 3000 | 13600 | 21000 | 0.15 | 0.95 | 2.25 | 5.8614 | 4.1955 | 2.7353 | 1840 | 1840 | 8400 | 15100 | 0.26 | 0.84 | 1.89 | 2.074 | 2.9307 | 2.3415 | 1430 | 1430 | 6500 | 12500 | 0.25 | 0.68 | 1.59 | 1.6764 | 2.8014 | 2.304 |  | 0.59524 | 0.96154 |  | Integrated | 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10095215 | MUZ-GL09NA-U1 | MSZ-GL09NA-U1 | HRCU-A-CB-O | 12.8 | 24.6 | 15.4 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4500 | 10900 | 15900 | 0.23 | 0.72 | 1.25 | 5.734 | 4.4368 | 3.7279 |  | 2830 | 6700 | 10200 | 0.28 | 0.63 | 1.06 | 2.9621 | 3.1168 | 2.8201 |  | 2280 |  | 8000 | 0.24 |  | 0.85 | 2.7842 |  | 2.7583 |  | 0.50314 | 0.85714 |  | MAC-640BH-U | 130 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715783 | MUZ-GL12NA-U1 | MSZ-GL12NA-U1 | HRCU-A-CB-O | 12.5 | 23.1 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 2000 | 14400 | 18100 | 0.11 | 1.1 | 1.62 | 5.3286 | 3.8366 | 3.2744 |  | 1150 | 9200 | 12000 | 0.13 | 0.87 | 1.24 | 2.5926 | 3.0991 | 2.8362 |  | 1040 |  | 10200 | 0.1 |  | 1.02 | 3.0479 |  | 2.9307 |  | 0.56354 | 0.76923 |  | MAC-640BH-U | 130 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715784 | MUZ-GL15NA-U1 | MSZ-GL15NA-U1 | HRCU-A-CB-O | 11.7 | 21.6 | 13 | 14000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4800 | 18000 | 20900 | 0.2 | 1.6 | 2.01 | 7.0337 | 3.297 | 3.0474 |  | 2150 | 12200 | 16400 | 0.2 | 1.6 | 2.01 | 3.1505 | 2.2347 | 2.3912 |  | 2080 |  | 14100 | 0.24 |  | 1.57 | 2.5399 |  | 2.632 |  | 0.67464 | 1.2 |  | MAC-640BH-U | 130 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715785 | MUZ-GL18NA-U1 | MSZ-GL18NA-U1 | HRCU-A-CB-O | 11.2 | 20.5 | 13.4 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 5400 | 21600 | 25000 | 0.32 | 1.68 | 2.5 | 4.9456 | 3.7681 | 2.9307 |  | 2780 | 13800 | 18200 | 0.37 | 1.48 | 2.15 | 2.202 | 2.7327 | 2.4809 |  | 2590 |  | 15100 | 0.32 |  | 1.88 | 2.372 |  | 2.3539 |  | 0.604 | 0.86486 |  | MAC-642BH-U1 | 120 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10053547 | PUZ-A24NHA7 | PLA-A24EA7 | HRCU-A-CB-O | 11.2 | 24.2 | 14.3 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 9000 | 26000 | 29000 | 0.45 | 1.75 | 2.07 | 5.8614 | 4.3542 | 4.1058 |  | 5100 | 14900 | 16600 | 0.42 | 1.6 | 1.9 | 3.5587 | 2.7292 | 2.5605 |  | 4500 |  | 13000 | 0.4 |  | 1.4 | 3.297 |  | 2.7214 |  | 0.44828 | 0.95238 |  | N/A |  |  |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10054648 | PUZ-A36NKA7 | PLA-A36EA7 | HRCU-A-CB-O | 10.4 | 21.8 | 12.9 | 36000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 18000 | 38000 | 42000 | 0.94 | 3.54 | 3.02 | 5.612 | 3.146 | 4.0758 |  | 10000 | 22000 | 24000 | 0.93 | 2.49 | 3 | 3.1513 | 2.5894 | 2.3446 |  | 9200 |  | 21600 | 0.83 |  | 2.6 | 3.2485 |  | 2.4347 |  | 0.51429 | 0.89247 |  | N/A |  |  |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8797134 | MUZ-FH18NAH2 | MSZ-FH18NA | HRCU-A-CB-O | 11 | 21 | 12.5 | 17200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) |  | 7540 | 20300 | 30400 | 0.85 | 1.77 | 3.4 | 2.5997 | 3.3612 | 2.6204 | 4300 | 4300 | 12480 | 24300 | 0.6 | 1.25 | 3.39 | 2.1003 | 2.926 | 2.1008 | 3700 | 3700 | 9640 | 20900 | 0.53 | 0.98 | 2.98 | 2.046 | 2.8829 | 2.0554 |  | 0.6875 | 0.88333 |  | Integrated | 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | -13 | 2640 |  | 14900 | 0.54 |  | 2.46 | 1.4328 |  | 1.7751
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8854558 | MUFZ-KJ15NAHZ | MFZ-KJ15NA | HRCU-A-CB-O | 11.6 | 21.8 | 13.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Floor Mount) |  | 5100 | 18000 | 25000 | 0.7 | 1.41 | 3.41 | 2.1352 | 3.7413 | 2.1486 | 3540 | 3540 | 14400 | 20000 | 0.44 | 1.19 | 3.04 | 2.3579 | 3.5464 | 1.9281 | 3190 | 3190 |  | 18000 | 0.4 |  | 2.83 | 2.3372 |  | 1.8641 |  | 0.72 | 0.90909 |  | Integrated | 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 8797130 | MUZ-FH06NA | MSZ-FH06NA | HRCU-A-CB-O | 13.5 | 33.1 | 19 | 6000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 1600 | 8700 | 14000 | 0.11 | 0.55 | 1.27 | 4.26 | 4.68 | 3.23 |  | 920 | 5900 | 10700 | 0.08 | 0.5 | 1 | 3.37 | 3.46 | 3.13 |  | 640 |  | 8700 | 0.06 |  | 0.91 | 3.13 |  | 2.8 |  | 0.62143 | 0.81308 |  | Accessory (MAC-640BH-U) | 106W @208V; 130W @230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | -13 | 240 | z | 6400 | 0.03 |  | 0.8 | 2.34 |  | 2.34
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr.Slim FH Series | 8797132 | MUZ-FH06NAH | MSZ-FH06NAH | HRCU-A-CB-O | 12.5 | 33.1 | 19 | 6000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 1600 | 8700 | 14000 | 0.11 | 0.55 | 1.27 | 4.26 | 4.68 | 3.23 |  | 920 | 5900 | 10700 | 0.21 | 0.628 | 1.13 | 1.28 | 2.75 | 2.78 |  | 640 |  | 8700 | 0.19 |  | 1.04 | 0.99 |  | 2.45 |  | 0.62143 | 0.81308 |  | Integrated | 106W @208V; 130W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A | 240 |  | 2100 | 0.16 |  | 0.93 | 0.44 |  | 2.02
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 8797133 | MUZ-FH18NA2 | MSZ-FH18NA2 | HRCU-A-CB-O | 12 | 21 | 12.5 | 17200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 5150 | 20300 | 30000 | 0.43 | 1.72 | 3.39 | 3.51 | 3.46 | 2.59 |  | 2950 | 13700 | 20300 | 0.31 | 1.32 | 2.8 | 2.79 | 3.04 | 2.12 |  | 2050 |  | 20300 | 0.23 |  | 2.96 | 2.61 |  | 2.01 |  | 0.67667 | 1 |  | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | -13 | 750 | z | 14000 | 0.11 |  | 2.35 | 2 |  | 1.74
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series; KJ-Series | 8849446 | MUFZ-KJ12NAHZ | MFZ-KJ12NA | HRCU-A-CB-O | 12 | 25.5 | 13.6 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 2900 | 13000 | 22800 | 0.27 | 0.9 | 2.39 | 3.15 | 4.23 | 2.8 |  | 1650 | 8800 | 14800 | 0.2 | 0.93 | 1.89 | 2.42 | 2.77 | 2.29 |  | 1150 |  | 13000 | 0.15 |  | 1.81 | 2.25 |  | 2.1 |  | 0.57018 | 0.87838 |  | Integrated | 106W @208V; 130W @ 230 V |  |  | -13 | 420 | z | 8000 | 0.07 |  | 1.28 | 1.76 |  | 1.83
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 8854557 | MUFZ-KJ09NAHZ | MFZ-KJ09NA | HRCU-A-CB-O | 13 | 28.2 | 15.8 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 2900 | 11000 | 19000 | 0.27 | 0.75 | 2.37 | 3.15 | 4.3 | 2.35 |  | 1650 | 7500 | 13400 | 0.2 | 0.8 | 1.86 | 2.42 | 2.75 | 2.11 |  | 1150 |  | 11000 | 0.15 |  | 1.6 | 2.25 |  | 2.01 |  | 0.57895 | 0.8209 |  | Integrated | 106W @208V; 130W @ 230 V |  |  | -13 | 420 | z | 7000 | 0.07 |  | 1.27 | 1.76 |  | 1.62
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 8854559 | MUFZ-KJ18NAHZ | MFZ-KJ18NA | HRCU-A-CB-O | 11.3 | 21 | 12.6 | 17000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 5700 | 21000 | 29000 | 0.48 | 1.73 | 3.43 | 3.48 | 3.56 | 2.48 |  | 3250 | 12800 | 23000 | 0.35 | 1.43 | 3.21 | 2.72 | 2.62 | 2.1 |  | 2260 |  | 21000 | 0.26 |  | 3 | 2.55 |  | 2.05 |  | 0.72414 | 0.91304 |  | Integrated | 98W @208V; 120W @ 230 V |  |  | -13 | 840 | z | 15700 | 0.13 |  | 2.3 | 1.89 |  | 2
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 4217888 | MUZ-FE18NA | MSZ-FE18NA | N/A | 10.3 | 20.2 | 14.2 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) |  | 7500 | 21600 | 29700 | 0.52 | 1.54 | 2.42 | 4.23 | 4.11 | 3.6 |  | 4300 | 11700 | 25850 | 0.37 | 1.24 | 3.28 | 3.41 | 2.76 | 2.31 |  | 3000 |  | 21830 | 0.28 |  | 3.15 | 3.14 |  | 2.03 |  | 0.73502 | 0.84449 |  | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. |  | N/A |  | z
Panasonic | Panasonic | RAC Multi E | 10221199 | CU-3E19RBU-5 | Non-Ducted Indoor Unit | HMSV-A-CB | 10.5 | 22 | 12.55 | 19000 | Yes | Ductless | Multi-zone | Non-ducted indoor units |  | 5500 | 26000 | 28400 | 0.32 | 2.06 | 2.3 | 5 | 3.7 | 3.61 |  | 4100 | 19800 | 20800 | 0.37 | 2.37 | 2.85 | 3.2496 | 2.45 | 2.1402 |  | 3800 |  | 18900 | 0.37 |  | 2.64 | 3.01 |  | 2.1 |  | 0.66549 | 0.90865 |  | Accessory for outdoor unit CU-3E19RBU-5; Wind Baffle # WINDB-M1 |  |  |  | -5°F | 2000 |  | 10500 | 0.26 |  | 1.85 | 2.26 |  | 1.66
Panasonic | Panasonic | Exterios-Series | 7958198 | CS-E9RKUA | CU-E9RKUAW | HRCU-A-CB-O | 11 | 23 | 13 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4100 | 12000 | 14100 | 0.2 | 1.12 | 1.5 | 6 | 3.14 | 2.76 |  | 3200 | 8100 | 9500 | 0.19 | 0.99 | 1.33 | 4.939 | 2.3994 | 2.1 |  | 2400 |  | 8300 | 0.16 |  | 1.32 | 4.3988 |  | 1.844 |  | 0.58865 | 0.87368 |  | N/A |  |  |  | -5°F | 1600 |  | 7000 | 0.13 |  | 1.31 | 3.6093 |  | 1.567
Panasonic | Panasonic | Exterios-Series | 7958199 | CS-E12RKUA | CU-E12RKUAW | HRCU-A-CB-O | 11 | 22.5 | 12.5 | 11500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4100 | 13800 | 16300 | 0.2 | 1.25 | 1.71 | 6 | 3.24 | 2.79 |  | 3200 | 8900 | 10500 | 0.19 | 1.05 | 1.44 | 4.939 | 2.4857 | 2.14 |  | 2400 |  | 9100 | 0.16 |  | 1.51 | 4.3988 |  | 1.7673 |  | 0.55828 | 0.86667 |  | N/A |  |  |  | -5°F | 1600 |  | 7900 | 0.13 |  | 1.6 | 3.6093 |  | 1.4479
Panasonic | Panasonic | Exterios E:Deluxe | 7958200 | CS-E18RKUA | CU-E18RKUAW | HRCU-A-CB-O | 10 | 19.5 | 13.2 | 17200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 5800 | 21600 | 22000 | 0.38 | 1.75 | 1.8 | 4.47 | 3.62 | 3.57 |  | 3400 | 11600 | 12000 | 0.34 | 1.3 | 1.35 | 2.9326 | 2.6167 | 2.6 |  | 2600 |  | 10100 | 0.3 |  | 1.32 | 2.5415 |  | 2.2438 |  | 0.45909 | 0.84167 |  | N/A |  |  |  | -5°F | 1900 |  | 8200 | 0.26 |  | 1.29 | 2.143 |  | 1.8641
Panasonic | Panasonic | Exterios XE | 8860533 | CU-XE9SKUA | CS-XE9SKUA | HRCU-A-CB-O | 14 | 30.6 | 17.05 | 8700 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3000 | 10900 | 18000 | 0.15 | 0.67 | 1.65 | 5.93 | 4.78 | 3.21 |  | 2100 | 8000 | 11000 | 0.14 | 0.75 | 1.38 | 4.3988 | 3.1261 | 2.34 |  | 1700 |  | 11000 | 0.12 |  | 1.73 | 4.1544 |  | 1.86 |  | 0.61111 | 1 |  | included with outdoor unit CU-XE9SKUA | 510 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F |  | -5°F | 1300 |  | 10400 | 0.1 |  | 1.72 | 3.8123 |  | 1.7732
Panasonic | Panasonic | Exterios XE | 8861565 | CU-XE12SKUA | CS-XE12SKUA | HRCU-A-CB-O | 12.5 | 26.2 | 14.7 | 11500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3000 | 13600 | 23000 | 0.15 | 0.95 | 2.1 | 5.93 | 4.1955 | 3.2 |  | 2100 | 10400 | 12500 | 0.14 | 1.05 | 1.6662 | 4.3988 | 2.9028 | 2.2 |  | 1700 |  | 12500 | 0.12 |  | 1.99 | 4.1544 |  | 1.84 |  | 0.54348 | 1 |  | included with outdoor unit CU-XE12SKUA | 780 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F |  | -5°F | 1300 |  | 11800 | 0.1 |  | 2.01 | 3.8123 |  | 1.7216
Panasonic | Panasonic | Low-Profile Ducted | 9125308 | CU-E9SD3UA | CS-E9SD3UAW | HRCU-A-CB-O | 10 | 20.5 | 13 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4100 | 9000 | 10200 | 0.25 | 0.69 | 0.85 | 4.8 | 3.82 | 3.53 |  | 3200 | 7900 | 9000 | 0.23 | 0.91 | 1.12 | 4.0801 | 2.5458 | 2.36 |  | 2400 |  | 7800 | 0.2 |  | 1.11 | 3.5191 |  | 2.0607 |  | 0.76471 | 0.86667 |  | N/A |  |  |  | -5°F | 1600 |  | 6700 | 0.16 |  | 1.1 | 2.9326 |  | 1.7862
Panasonic | Panasonic | Low-Profile Ducted | 9125309 | CU-E12SD3UA | CS-E12SD3UAW | HRCU-A-CB-O | 10 | 20 | 12.5 | 11500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 4100 | 11500 | 13300 | 0.25 | 0.92 | 1.15 | 4.8 | 3.64 | 3.39 |  | 3200 | 9500 | 11000 | 0.23 | 1.15 | 1.44 | 4.0801 | 2.4225 | 2.24 |  | 2400 |  | 9600 | 0.2 |  | 1.52 | 3.5191 |  | 1.8521 |  | 0.7218 | 0.87273 |  | N/A |  |  |  | -5°F | 1600 |  | 8200 | 0.16 |  | 1.6 | 2.9326 |  | 1.5029
Panasonic | Panasonic | Wall Mounted | 9571162 | CU-XE15SKUA | CS-XE15SKUA | HRCU-A-CB-O | 12 | 22.1 | 12.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) |  | 3300 | 18000 | 24000 | 0.2 | 1.3 | 2.65 | 4.9 | 4.06 | 2.65 |  | 2000 | 11000 | 16500 | 0.16 | 1.02 | 2.3 | 3.6657 | 3.16 | 2.1 |  | 1500 |  | 15700 | 0.15 |  | 2.32 | 2.9326 |  | 1.98 |  | 0.65417 | 0.95152 |  | included with outdoor unit (Replacement part # CWA341072) | 100 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F |  | -5°F | 1100 |  | 14900 | 0.13 |  | 2.34 | 2.4814 |  | 1.8673

## Sheet1
AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | COP at Min. Capacity 17°F | COP at Rated Capacity 17°F | COP at Max. Capacity 17°F
ahri | out_model | in_model | cap_min | cap_rated | cap_max | cop_min | cop_rated | cop_max
8004699 | AOU9RLS3 | ASU9RLS3 | 2286 | 7000 | 16000 | 3.19 | 3.46 | 2.28
8703348 | AOU9RLS3 | ASU9RLS3Y | 2286 | 7000 | 16000 | 3.19 | 3.46 | 2.28
8703349 | AOU9RLS3H | ASU9RLS3Y | 2286 | 7000 | 16000 | 1.86 | 3.36 | 2.12
8004700 | AOU9RLS3H | ASU9RLS3 | 2286 | 7000 | 16000 | 1.86 | 3.36 | 2.12
7993242 | AOU12RLS3 | ASU12RLS3 | 2491 | 9600 | 17500 | 3.48 | 3.3 | 2.49
8703350 | AOU12RLS3 | ASU12RLS3Y | 2491 | 9600 | 17500 | 3.48 | 3.3 | 2.49
8703506 | AOU12RLS3H | ASU12RLS3Y | 2491 | 9600 | 17500 | 2.03 | 3.18 | 2.32
7993244 | AOU12RLS3H | ASU12RLS3 | 2491 | 9600 | 17500 | 2.03 | 3.18 | 2.32
8703507 | AOU15RLS3 | ASU15RLS3Y | 2798 | 11200 | 21500 | 4.1 | 3.14 | 2.43
7993243 | AOU15RLS3 | ASU15RLS3 | 2798 | 11200 | 21500 | 4.1 | 3.14 | 2.43
6961728 | AOU9RLFW1 | ASU9RLF1 | 1079 | 7600 | 9500 | 1.59 | 3.1363 | 2.1917
8718495 | AOU18RLXFW1 | ASU18RLF | 5485 | 14600 | 22759 | 3.83 | 3.08 | 2.34
8703508 | AOU15RLS3H | ASU15RLS3Y | 2798 | 11200 | 21500 | 2.34 | 3.06 | 2.3
7993245 | AOU15RLS3H | ASU15RLS3 | 2798 | 11200 | 21500 | 2.34 | 3.06 | 2.3
8779045 | AOU18RLXFWH | ASU18RLF | 5485 | 14600 | 22759 | 2.82 | 3.02 | 2.22
7937663 | AOU18RLB | ASU18RLB | 2798 | 11500 | 16700 | 4.0991 | 2.92 | 2.3327
5751311 | AOU9RLFC | AUU9RLF | 2744 | 9400 | 16100 | 5.65 | 2.88 | 2.66
5751312 | AOU9RLFC | ARU9RLF | 2744 | 9400 | 16100 | 5.65 | 2.88 | 2.66
6961729 | AOU12RLFW1 | ASU12RLF1 | 1795 | 9400 | 11200 | 2.8 | 2.869 | 2.196
8693477 | AOU48RLAVM | Non-Ducted Indoor Units | 15400 | 33000 | 50000 | 4.5134 | 2.84 | 3.2856
8693480 | AOU36RLAVM | Non-Ducted Indoor Units | 16460 | 25800 | 42000 | 4.021 | 2.8 | 2.7786
6936995 | AOU9RLFF | AGU9RLF | 2320 | 7500 | 14000 | 3.4 | 2.8 | 2.25
6937309 | AOU9RLFFH | AGU9RLF | 2320 | 7500 | 14000 | 1.94 | 2.8 | 2.08
5063326 | AOU12RLS2 | ASU12RLS2 | 2491 | 10200 | 17900 | 3.65 | 2.72 | 2.63
8908615 | AOU36RLXFZH | Non-Ducted Indoor Units | 11212 | 21400 | 39341 | 3.02 | 2.64 | 2.25
6937311 | AOU15RLFFH | AGU15RLF | 2832 | 11600 | 19000 | 1.77 | 2.62 | 1.83
6936997 | AOU15RLFF | AGU15RLF | 2832 | 11600 | 19000 | 2.59 | 2.62 | 1.93
8033586 | AOU24RLXFZH | Non-Ducted Indoor Units | 6005 | 15400 | 26000 | 2.84 | 2.6 | 2.13
6936996 | AOU12RLFF | AGU12RLF | 2457 | 10600 | 15000 | 3 | 2.6 | 2.02
8033584 | AOU18RLXFZH | Non-Ducted Indoor Units | 6619 | 14200 | 23500 | 2.4 | 2.6 | 2.16
6937310 | AOU12RLFFH | AGU12RLF | 2457 | 10600 | 15000 | 1.85 | 2.6 | 1.89
5751313 | AOU12RLFC | AUU12RLF | 2793 | 10200 | 17600 | 4.76 | 2.58 | 2.41
5751314 | AOU12RLFC | ARU12RLF | 2793 | 10200 | 17600 | 4.76 | 2.58 | 2.41
5063325 | AOU9RLS2 | ASU9RLS2 | 2320 | 9400 | 16400 | 3.4 | 2.54 | 2.45
8912454 | AOU30RLXEH | ASU30RLE | 7570 | 21400 | 35200 | 4.2 | 2.49 | 2.29
8718545 | AOU24RLXFW1 | ASU24RLF | 5740 | 16720 | 27700 | 3.44 | 2.49 | 2.36
8779046 | AOU24RLXFWH | ASU24RLF | 5740 | 16720 | 27700 | 2.63 | 2.32 | 2.26